**Troubleshooting Phoenix Firebird**

**Blower not running**

1. Unit unplugged or no power to outlet – plug in to outlet or use a different outlet
2. Power Switch not working or set to THERMOSTAT and no thermostat connected or thermostat is not calling for heat – connect thermostat and retry, test power switch and thermostat, repair or replace as needed.
3. Blower relay not operating – test and replace relay as needed.
4. Wiring fault inside device – inspect and repair wiring
5. Defective blower or blower capacitor – test and replace as needed

**Blower running but no heat**

1. Airflow restricted – remove restrictions
2. High temperature limit reached (140°F) – turn off and allow to cool
3. Heating contactor(s) not opening – test and replace as needed
4. Wiring fault inside device – inspect and repair wiring
5. Defective heating element, pressure switch, or temperature limit switch – test and replace as needed.